## EPM2200
Reference | Enclosure Option | EPM2200 Option | EPM2200 Communications | Description | Dependency Expression | Rule Type
PL2200
| ENC120 |  |  | NEMA1 Rated - Indoor, Single Meter Enclosure, 120V
| ENC277 |  |  | NEMA1 Rated - Indoor, Single Meter Enclosure, 277V
| ENN120 |  |  | NEMA4X Rated - Indoor/Outdoor, Single Meter Enclosure, 120V
| ENN277 |  |  | NEMA4X Rated - Indoor/Outdoor, Single Meter Enclosure, 277V
| XXXXXX |  |  | None
|  | A1 |  | Volts and Amps meter
|  | B1 |  | Volts, Amps, Power and Frequency meter
|  | C1 |  | Volts, Amps, Power, Frequency and Energy Counters meter
|  | BN |  | BACnet Volts, Amps, Power, Frequency and Energy Counters meter
|  |  | S | RS485 Serial/KYZ Pulse | A1 OR B1 OR C1 | required
|  |  | X | None | A1 OR B1 OR C1 | required
|  |  | B | BACnet MS/TP Serial and Modbus TCP/IP Ethernet | BN | required
If "EPM 2200 Option" BN: BACnet Volts, Amps, Power, Frequency and Energy Counters meter is chosen only the EPM 2200 Communications 'B' option is available
If EPM 2200 Option A1,B1,C1 is chosen only the EPM 2200 Communications 'S' option or 'X' None will be available
[7 empty] | # | Name | Description | EI Part Number | GE Part Number
[7 empty] | 1 | DIN Bracket | DIN Mounting Brackets | E145355-1 | PL2200-ACC-DIN
Reference = Model ?

## EPM4600
Reference | Enclosure | Enclosure | Feed Configuration | Frequency | Current Inputs | Software | Communications | Enclosure Protocol Addon | EPM 4600 Displays | Description | Dependency Expression | Rule Type
PL4600
| ENC350 | ssss | [7 empty] | Meter Enclosure with 3.5" display
| ENC570 | ddd | [7 empty] | Meter Enclosure with 5.7" display
| ENP001 | fff | [7 empty] | Panel Mount - Design 1
| XXXXXX | ggg | [7 empty] | None
|  |  | T | [6 empty] | Three Phase
|  |  | S | [6 empty] | Single Phase
|  |  |  | 5 | [5 empty] | 50 Hz
|  |  |  | 6 | [5 empty] | 60 Hz
[5 empty] | 10A |  |  |  |  | Up to 10A Current
[5 empty] | 02A |  |  |  |  | Up to 2A Current
[6 empty] | A |  |  |  | Transducer
[6 empty] | B |  |  |  | Basic Logging - 2MB Memory
[6 empty] | C |  |  |  | Advanced Logging - 32 MB Memory
[7 empty] | S |  |  | Serial (RS485) Modbus
[7 empty] | W |  |  | WiFi, RJ45 100BaseT Ethernet
[8 empty] | XXX |  | None
[8 empty] | PBA |  | Enclosure Serial BACNet Protocol Converter (Requires S Communications option. Cannot be ordered with Communications option W)
[8 empty] | PLW |  | Enclosure Serial LonWorks Protocol Converter (Requires S Communications option. Cannot be ordered with Communications option W)
[9 empty] | PL4600-DIS3500 | 3.5" Touch Screen Display with Installation Kit
[9 empty] | PL4600-DIS5700 | 5.7" Touch Screen Display with Installation Kit
[13 empty] | Order Codes | EPM4600
[13 empty] | P&L | Sub P&L | Sub Business | Product Platform | Product Group
[13 empty] | GRID AUTOMATION | PROTECTION & CONTROL | INDUSTRIAL - METERS | METERS | EPM 4600
EPM 4600 Accessories
[13 empty] | Name | GE Part Number | Description
Display Cable
[14 empty] | PL4600-ACC-DC1 | EPM 4600 Display Cable Only - 10ft (120") Length
WiFi Antenna
[14 empty] | PL4600-ACC-WFA | Remote mounted antenna kit with antenna and magnetic base
Protocol Addon
[14 empty] | PL4600-ACC-PBA | Serial BACNet Protocol Converter (Requires S Communications option. Cannot be ordered with Communications option W)
[14 empty] | PL4600-ACC-PLW | Serial LonWorks Protocol Converter (Requires S Communications option. Cannot be ordered with Communications option W)
Current Transformers (CTs)
[14 empty] | PL4600-ACC-C12 | Current Transformer Rectangular 1200:1A ,4.63 VA, 3.65" x 1.75" window, 5' 16AWG leads. Accuracy 0.3% as per IEEE C57.13-2008.
[14 empty] | PL4600-ACC-C60 | Current Transformer Rectangular 600:1A, 2.63VA, current transformer, 2.53" x 1.3" window, 5' 16AWG leads. Accuracy 0.3% as per IEEE C57.13-2008.
[14 empty] | PL4600-ACC-C25 | Current Transformer Toroid 250:1A, 4.5VA,0.64" ID, 5' 14AWG Leads. Accuracy 0.3% as per IEEE C57.13-2008.
[14 empty] | PL4600-ACC-C10 | Current Transformer Toroid 100:1A, 4.5VA, 0.64" ID, 5' 14AWG Leads. Accuracy 0.3% as per IEEE C57.13-2008.
Power Supply
[14 empty] | PL4600-ACC-PS1 | Power Supply TDK-Lambda America DSP30-24/277A

## EPM6000
Reference | Enclosure Option | Hz | Amp | THD and Pulse | Substitute LV Power Supply | Ethernet Option | Description | Dependency Expression | Rule Type
PL6000 | [6 empty] | EPM 6000 - Multi-Function Power Metering System
| ENC120 | [5 empty] | NEMA1 Rated - Indoor, Single Meter Enclosure, 120V
| ENC277 | [5 empty] | NEMA1 Rated - Indoor, Single Meter Enclosure, 277V
| ENN120 | [5 empty] | NEMA4X Rated - Indoor/Outdoor, Single Meter Enclosure, 120V
| ENN277 | [5 empty] | NEMA4X Rated - Indoor/Outdoor, Single Meter Enclosure, 277V
| ENS001 | [5 empty] | EPM Retrofit Panel Adapter - SWDGS5-E67-M
| ENS002 | [5 empty] | EPM Retrofit Panel Adapter - SWDGL9-E67-M
| ENS003 | [5 empty] | EPM Retrofit Panel Adapter - SWDGS9-E67-EPM
| ENS004 | [5 empty] | EPM Retrofit Panel Adapter - SWDG435-SK-M
| XXXXXX | [5 empty] | None
|  | 5 |  |  |  |  | 50 Hz Frequency System
|  | 6 |  |  |  |  | 60 Hz Frequency System
|  |  | 1A |  |  |  | 1 Amp Secondry CT input
|  |  | 5A |  |  |  | 5 Amp Secondry CT input
|  |  |  | THD |  |  | THD, Modbus Alarms & One KYZ pulse Output
|  |  |  | 0 |  |  | No THD Option
[5 empty] | - |  | No LDC
[5 empty] | LDC |  | Low Voltage DC Power Supply
[6 empty] | S | Serial Port Communication
[6 empty] | E | 10/100 RJ45 Ethernet Port
None of the enclosure options are available when Power Supply LDC is selected
[10 empty] | GE Part Number | Description
[10 empty] | PL6000-ACC-DIN | DIN Mounting Bracket

## EPM6010
Reference | Enclosure Option | Frequency | Current Inputs | Software | Power Supply | Description | Dependency Expression | Rule Type
PL6010 | [5 empty] | BACnet Meter
| ENC120 |  |  |  |  | NEMA1 Rated - Indoor, Single Meter Enclosure, 120V
| ENC277 |  |  |  |  | NEMA1 Rated - Indoor, Single Meter Enclosure, 277V
| ENN120 |  |  |  |  | NEMA4X Rated - Indoor/Outdoor, Single Meter Enclosure, 120V
| ENN277 |  |  |  |  | NEMA4X Rated - Indoor/Outdoor, Single Meter Enclosure, 277V
| XXXXXX |  |  |  |  | None
|  | 5 |  |  |  | 50Hz
|  | 6 |  |  |  | 60Hz
|  |  | 5A |  |  | 5 Amps
|  |  | 1A |  |  | 1 Amp
|  |  |  | THD |  | THD, Limits, Alarms & One KYZ pulse output
[5 empty] | HI | Universal (90-265)VAC or (100-370)VDC
[5 empty] | LDC | DC Power Supply (18-60)VDC
None of the enclosure option are available when Power Supply LDC is selected

## EPM7000
Reference | Enclosure Option | Freq | Current Inputs | Software | Power Supply | I/O Slot 1 | I/O Slot 2 | Description | Dependency Expression | Rule Type
PL7000
| ENC120 | [6 empty] | NEMA1 Rated - Indoor, Single Meter Enclosure, 120V
| ENC277 | [6 empty] | NEMA1 Rated - Indoor, Single Meter Enclosure, 277V
| ENN120 | [6 empty] | NEMA4X Rated - Indoor/Outdoor, Single Meter Enclosure, 120V
| ENN277 | [6 empty] | NEMA4X Rated - Indoor/Outdoor, Single Meter Enclosure, 277V
| ENS001 | [6 empty] | EPM Retrofit Panel Adapter - SWDGS5-E67-M
| ENS002 | [6 empty] | EPM Retrofit Panel Adapter - SWDGL9-E67-M
| ENS003 | [6 empty] | EPM Retrofit Panel Adapter - SWDGS9-E67-EPM
| ENS004 | [6 empty] | EPM Retrofit Panel Adapter - SWDG435-SK-M
XXXXXX
|  | 5 | ¦ | ¦ | ¦ | ¦ | ¦ | 50 Hz AC frequency system
|  | 6 | ¦ | ¦ | ¦ | ¦ | ¦ | 60 Hz AC frequency system
|  |  | 5A | ¦ | ¦ | ¦ | ¦ | 10 Amp Secondary
|  |  | 1A | ¦ | ¦ | ¦ | ¦ | 2 Amp Secondary
|  |  |  | A | ¦ | ¦ | ¦ | Multimeter Function Only
|  |  |  | B | ¦ | ¦ | ¦ | Data Logging Memory
|  |  |  | C | ¦ | ¦ | ¦ | Power Quality Harmonics
|  |  |  | D | ¦ | ¦ | ¦ | Limits and Control
|  |  |  | E | ¦ | ¦ | ¦ | 64 Samples/Cycle Waveform Recording
|  |  |  | F | ¦ | ¦ | ¦ | 512 Samples/Cycle Waveform Recording
[5 empty] | HI | ¦ | ¦ | 90-265VAC/VDC
[5 empty] | LDC | ¦ | ¦ | 18-60VDC
[6 empty] | X | X | None
[6 empty] | E1 | E1 | 100BaseT Ethernet
[6 empty] | E2 | E2 | 100BaseT Ethernet with IEC 61850 Protocol
[6 empty] | C1 | C1 | Four Channel Bi-directional 0-1mA Outputs
[6 empty] | C20 | C20 | Four Channel Bi-directional 4-20mA Outputs
[6 empty] | RS1 | RS1 | Two Relay status Outputs / Two Status Inputs
[6 empty] | PS1 | PS1 | Four Pulse Outputs / Four Status Inputs
[6 empty] | F1 | F1 | Fiber Optic Interface with ST Terminations
[6 empty] | F2 | F2 | Fiber Optic interface with Versatile Terminations
Enclosures are not available when Power Supply LDC is selected
GE Confidential

## EPM 7000P
Model | Enclosure Option | Frequency | Current Inputs | Software | Power Supply | I/O Slot 1 | I/O Slot 2 | Description | Dependency Expression | Rule Type
PL7000P | [7 empty] | EPM 7000P Power Quality Meter
| XXXXXX | [6 empty] | None
| ENC120 | [6 empty] | NEMA1 Rated - Indoor, Single Meter Enclosure, 120V
| ENC277 | [6 empty] | NEMA1 Rated - Indoor, Single Meter Enclosure, 277V
| ENN120 | [6 empty] | NEMA4X Rated - Indoor/Outdoor, Single Meter Enclosure, 120V
| ENN277 | [6 empty] | NEMA4X Rated - Indoor/Outdoor, Single Meter Enclosure, 277V
| ENS001 | [6 empty] | EPM Retrofit Panel Adapter - SWDGS5-E67-M
| ENS002 | [6 empty] | EPM Retrofit Panel Adapter - SWDGL9-E67-M
| ENS003 | [6 empty] | EPM Retrofit Panel Adapter - SWDGS9-E67-EPM
| ENS004 | [6 empty] | EPM Retrofit Panel Adapter - SWDG435-SK-M
| CON001 | [6 empty] | Conformal Coating Option
|  | 6 | [5 empty] | 60 Hz AC frequency system
|  | 5 | [5 empty] | 50 Hz AC frequency system
|  |  | 5A |  |  |  |  | 10 Amp Secondary
|  |  | 1A |  |  |  |  | 2 Amp Secondary
|  |  |  | A |  |  |  | Multimeter Function Only
|  |  |  | B |  |  |  | Data Logging, 2 MB Memory
|  |  |  | C |  |  |  | 128 Samples/Cycle Waveform Recording, 10 MB Memory
|  |  |  | D |  |  |  | 512 Samples/Cycle Waveform Recording, 128 MB Memory
[5 empty] | HI |  |  | 90-265 V AC/DC
[5 empty] | LD |  |  | 18-60 V DC
[6 empty] | XX | XX | None
[6 empty] | E1 | E1 | 100BaseT Ethernet
[6 empty] | E2 | E2 | 100BaseT Ethernet with IEC 61850 Protocol
[6 empty] | S1 | S1 | Serial RS232/RS485 Communications
[6 empty] | C1 | C1 | Four Channel Bi-directional 0-1mA Outputs
[6 empty] | C2 | C2 | Four Channel Bi-directional 4-20mA Outputs
[6 empty] | RS | RS | Two Relay status Outputs / Two Status Inputs
[6 empty] | PS | PS | Four Pulse Outputs / Four Status Inputs
[6 empty] | F1 | F1 | Fiber Optic Interface with ST Termination
[6 empty] | F2 | F2 | Fiber Optic interface with Versatile Link Termination
P&L
GRID AUTOMATION
Enclosures are not available when Power Supply LD is selected
If Software Option A is selected, for I/O Slot 1 or 2: E2 option is not available.
CON001 option only available for I/O Slot 1 or 2 options XX, E1, E2

## EPM 7000PT
Reference | Frequency | Current Inputs | Software | Power Supply | I/O Slot 1 | I/O Slot 2 | Description | Dependency Expression | Rule Type
PL7000PT | [6 empty] | EPM 7000PT Power Quality Meter Transducer
| 6 | [5 empty] | 60 Hz AC frequency system
| 5 | [5 empty] | 50 Hz AC frequency system
|  | 5A |  |  |  |  | 10 Amp Secondary
|  | 1A |  |  |  |  | 2 Amp Secondary
|  |  | A |  |  |  | Multimeter Function Only
|  |  | B |  |  |  | Data Logging, 2 MB Memory
|  |  | C |  |  |  | 128 Samples/Cycle Waveform Recording, 10 MB Memory
|  |  | D |  |  |  | 512 Samples/Cycle Waveform Recording, 128 MB Memory
|  |  |  | HI |  |  | 90-265 V AC/DC
|  |  |  | LD |  |  | 18-60 V DC
[5 empty] | XX | XX | None
[5 empty] | E1 | E1 | 100BaseT Ethernet
[5 empty] | E2 | E2 | 100BaseT Ethernet with IEC 61850 Protocol
[5 empty] | S1 | S1 | Serial RS232/RS485 Communications
[5 empty] | C1 | C1 | Four Channel Bi-directional 0-1mA Outputs
[5 empty] | C2 | C2 | Four Channel Bi-directional 4-20mA Outputs
[5 empty] | RS | RS | Two Relay status Outputs / Two Status Inputs
[5 empty] | PS | PS | Four Pulse Outputs / Four Status Inputs
[5 empty] | F1 | F1 | Fiber Optic Interface with ST Termination
[5 empty] | F2 | F2 | Fiber Optic interface with Versatile Link Termination
[10 empty] | P&L | Sub P&L | Sub Business | Product Platform | Product Group
[10 empty] | GRID AUTOMATION | PROTECTION & CONTROL | INDUSTRIAL - METERS | METERS | EPM 7000P
If Software Option A is selected, for I/O Slot 1 or 2: E2 option is not available.
GE Confidential

## EPM9700
Reference | X | Frequency | Control Power | Software |  |  |  | Description | Dependency Expression | Rule Type
PL9700
| X | [6 empty] | Reserved for Future Use
|  | 0 | [5 empty] | 60 Hz
|  | 1 | [5 empty] | 50 Hz
|  |  | 0 |  |  |  |  | Universal (100-240)VAC @50/60 Hz or (100-240)VDC
|  |  | 1 |  |  |  |  | 18-60 Volt DC Power Supply
|  |  |  | A |  |  |  | Standard: 512MB Memory, 512 Samples/Cycle
|  |  |  | B |  |  |  | Advanced: 1.2GB Memory, 1024 Samples/Cycle, IEC 61850
[5 empty] | X |  |  | Reserved for Future Use
[6 empty] | X |  | Reserved for Future Use
[7 empty] | X | Reserved for Future Use
GRID AUTOMATION
EPM 9700 - NPI

## EPM9000 Acc
PL9000 Accessories
Model Name | Description
PL9Display | PL9000 LED/LCD Display Module
GE Part Number |  | Description
PL9000 | P40NPLUS0 | P40NPlus Three line LED Display with 6ft cable
PL9000 | P70N00000 | P70N Color Touchscreen LCD Display with 6ft cable
Model Name (40 characters) | Description
EPM 9700 Accessories - P60 to P70N Adapter Plate | EPM 9700 - P60N to P70N Adapter Plate
GE Part Number |  | Description
PL9000 | ACC67A | EPM 9700 - P60N to P70N Adapter Plate
Model Name (40 characters) | Description
EPM 9700 Accessories - Display Bracket | EPM 9700 P70N Display ANSI Mounting Kit
GE Part Number |  | Description
PL9000 | ACC7AK | P70N Display ANSI Mounting Kit
Model Name | Description
PL9 Display Cable | PL9000 LED/LCD Display Cable
GE Part Number |  | Description
PL9000 | ACC406 | P40NPlus Display Cable only - 6 ft. length
PL9000 | ACC420 | P40NPlus Display Cable only - 20 ft. length
PL9000 | ACC706 | P70N Display Cable only - 6 ft. length
PL9000 | ACC720 | P70N Display Cable only - 20 ft. length
External Input/Output (I/O) Modules
GE Part Number |  | Description
Analog Output Modules
PL9000 | 1MAON4000 | 4 Channel 0-1 mA Analog Outputs
PL9000 | 1MAON8000 | 8 Channel 0-1 mA Analog Outputs
PL9000 | 20MAON400 | 4 Channel 4-20 mA Analog Outputs
PL9000 | 20MAON800 | 8 Channel 4-20 mA Analog Outputs
Analog Input Modules
PL9000 | 8AI100000 | 8 Channel 0-1mA Analog Inputs
PL9000 | 8AI200000 | 8 Channel 4-20mA Analog Inputs
PL9000 | 8AI300000 | 8 Channel 0-5V DC Analog Inputs
PL9000 | 8AI400000 | 8 Channel 0-10 V DC Analog Inputs
Digital Dry Contact Relay/Solid State Pulse Outputs
PL9000 | 4RO100000 | 4 Relay Outputs, 5A, 250VAC/30 VDC, Form C Latching
PL9000 | 4PO100000 | 4 Solid State Pulse Outputs, Form A or C KYZ Pulses, 20 Pulses/sec. Max.
Digital Status Inputs
PL9000 | 8DI100000 | 8 Channel Auxiliary Digital Status Inputs
I/O Power Supply
PL9000 | PSIO00000 | Auxiliary Power Supply (Required for External I/O Modules)
I/O Mounting Bracket
PL9000 | MBIO00000 | Mounting Bracket (Required for External I/O Modules)
EPM 9700 DIN Rail Mount Kit
GE Part Number |  | Description
PL9000 | ACCDIN | EPM 9700 DIN Rail Mount Kit
Note on A29: GE User: These are from the EPM 9000 (9450/9650) Brochure - copy the section Update the yellow highlighted cells with what is shown here. The EPM 9450/9650 Brochure needs to be changed as well.

## EPM9850
Reference | Frequency | Current Inputs | Power Supply | Form | Software Option | I/O Slot 1 | I/O Slot 2 | Description | Dependency Expression | Rule Type
PL9850 | [7 empty] | EPM 9850 - Revenue meter (Socket/Switchboard) with Power Quality
| 6 | [6 empty] | 60 Hz
| 5 | [6 empty] | 50 Hz
|  | 5 | [5 empty] | 5A Nominal CT Secondary
|  | 1 | [5 empty] | 1A Nominal CT Secondary
|  |  | S |  |  |  |  | Blade Powered - Not available for SWB3
|  |  | E |  |  |  |  | Externally Powered
|  |  |  | 9S |  |  |  | Rated Voltage 0-277 V L-N - 3E, 4W Wye Hook-up
|  |  |  | 3S |  |  |  | Rated Voltage 0-277 V L-N - 2.5E, 4W Wye w/ Neutral
|  |  |  | 4S |  |  |  | Rated Voltage 0-480 V L-L - 2E, 3W, Delta
|  |  |  | 9A |  |  |  | Rated Voltage 0-277 V L-N - A Base Form
|  |  |  | SB |  |  |  | Switchboard Case - Available with E & D Power Supply Only
[5 empty] | A |  |  | Multifunction Meter
[5 empty] | B |  |  | Standard Data Logging With Power Quality Harmonics
[5 empty] | C |  |  | 128 Samples/Cycle Waveform Recording, 10 MB Memory
[5 empty] | D |  |  | 512 Samples/Cycle Waveform Recording, 128 MB Memory
[6 empty] | XX | XX | None
[6 empty] | PS | PS | Four Pulse Outputs / Four Status Inputs
[6 empty] | RS | RS | Two Relay status Outputs / Two Status Inputs
[6 empty] | C1 | C1 | Four Channel Bi-directional 0-1mA Outputs
[6 empty] | C2 | C2 | Four Channel Bi-directional 4-20mA Outputs
[6 empty] | S1 | S1 | Serial RS232/RS485 Communications
[6 empty] | E1 | E1 | 100BaseT Ethernet
[7 empty] | E2 | 100BaseT Ethernet with IEC 61850 Protocol
[6 empty] | IB | IB | IRIG-B and 4 Pulse Outputs
[7 empty] | 4G | 4G LTE - Verizon Cert. Cell Modem (Not Available with SB - Switchboard Case)

## EPM9900P
Reference | Enclosure | Control Power | Frequency | Current Inputs | Software | Slot 1 | Slot 2 | Slot 3 | Slot 4 | Description | Dependency Expression | Rule Type
PL9900P
| ENC120 | [8 empty] | NEMA1 Rated - Indoor, Single Meter Enclosure, 120V
| ENC277 | [8 empty] | NEMA1 Rated - Indoor, Single Meter Enclosure, 277V
| ENC24E | [8 empty] | NEMA1 Rated - Indoor, Single Meter Enclosure, 18-60 VDC External Powered - Requires Control Power Option - LD
| ENC12E | [8 empty] | NEMA1 Rated - Indoor, Single Meter Enclosure, 120-240V AC/DC External Powered
| XXXXXX | [8 empty] | None
|  | AC | [7 empty] | 100-240VAC Power Supply
|  | HI | [7 empty] | 90‐265VAC or 100‐240VDC
|  | LD | [7 empty] | 18-60VDC (24-48VDC Systems)
|  |  | 6 | [6 empty] | 60 Hz
|  |  | 5 | [6 empty] | 50 Hz
|  |  |  | 5A | [5 empty] | 5A
|  |  |  | 1A | [5 empty] | 1A
[5 empty] | A |  |  |  |  | 512MB memory with 512 samples/cycle
[5 empty] | B |  |  |  |  | 1GB memory with 1024 samples/cycle, IEC 61850 Communications Protocol
[5 empty] | C |  |  |  |  | 4GB memory with 1024 samples/cycle, IEC 61850 Communications Protocol and 50MHz Transient Recording
[5 empty] | D |  |  |  |  | 512MB memory with 512 samples/cycle, Synchrophasor PMU
[5 empty] | E |  |  |  |  | 1GB memory with 1024 samples/cycle, IEC 61850 Communications Protocol, Synchrophasor PMU
[5 empty] | F |  |  |  |  | 4GB memory with 1024 samples/cycle, IEC 61850 Communications Protocol, 50MHz Transient Recording, Synchrophasor PMU
[6 empty] | S |  |  |  | 2-ports RS485 and 4 Pulse Outputs
[6 empty] | X |  |  |  | Empty Slot
[7 empty] | E1 |  |  | Second Ethernet Port - 10/100BaseTX, RJ45
[7 empty] | E2 |  |  | Second Ethernet Port - 100FX, Multimode ST Connector
[7 empty] | XX |  |  | Empty Slot
[8 empty] | R1 | R1 | 6 Relay Outputs
[8 empty] | D1 | D1 | 16 Status Inputs
[8 empty] | XX | XX | Empty Slot